## Start Here
Property Condition & 5-Year Capital Plan
Replace a visual impression with an operating and capital plan — what's damaged, what's aging, what to monitor, and what it will cost and when.
The property is an operating system. Roofs, doors, paving, drainage, climate control, security and access affect one another — one defect can create repair cost, customer disruption, lost rentals and insurance exposure at once. The repetition that makes a facility look simple is exactly why a small defect across 150 units becomes a capital project.
How to use this model
1. Set the PCA scope and engage specialists on tab 1 — decide who observes what, and note which conclusions are visual vs. tested.
2. Walk the site with tab 2, rating each component's condition by system (roof, doors, paving, climate, security, access…).
3. Track the records behind the visible condition on tab 3 (invoices, permits, warranties, logs, loss runs).
4. Enter each major component's age, remaining useful life, quantity and cost on tab 4 — the extended cost computes.
5. Tab 5 rolls those into a five-year capital plan with escalation, contingency and lost-rental impact, and a suggested reserve.
Legend
Amber cells are for you to fill in. Green cells are calculated. Don't overwrite them. Drop-downs offer preset lists.
Example rows are included on tabs 4–5 so the plan computes. Replace them with your facility's components.
Tabs
1. PCA Scope · 2. Inspection Checklist · 3. Records Request · 4. Component Register · 5. Five-Year Capital Plan · 6. Warning Signs
First Bank of the Lake · SBA Self-Storage Lending · (888) 828-5689 · fblake.bank
Not engineering advice. Cost opinions are screening estimates — confirm material items with local contractor quotes and qualified specialists. Remaining-useful-life figures are opinions, not guarantees. This content is provided for general informational purposes only and should not be considered legal, financial, tax, investment or lending advice. Financing options, approval requirements and transaction risks vary by borrower, property, lender and jurisdiction. Consult qualified legal, financial and lending professionals regarding your specific circumstances.

## 1. PCA Scope
STEP 1 — SCOPE THE ASSESSMENT, ENGAGE SPECIALISTS
PCA Scope & Specialists
A baseline PCA (ASTM E2018-24) often uses representative observations. Representative doesn't mean careless — the report should explain the sample and its limits.
SCOPE QUESTIONS TO SETTLE BEFORE THE INSPECTION
Question | Answer / commitment | Basis (visual / records / specialist)
How many buildings, roofs, units and doors will be observed?
Will all climate-controlled buildings be reviewed?
Will roofs be walked where safe and permitted?
Which building systems and specialty equipment are included?
Will records, permits, warranties and prior reports be reviewed?
Will the report identify immediate repairs AND five-year capital needs?
How will cost opinions be developed?
Which areas or systems are excluded?
When will specialist follow-up be recommended?
SPECIALISTS — ENGAGE WHEN CONDITION CALLS FOR IT
Specialist | Engaged? | Trigger / area of concern
Roofing professional
Structural engineer
Civil engineer (drainage/paving)
HVAC contractor
Electrician
Fire-protection professional
Elevator specialist
Accessibility (ADA) professional
Security-system vendor
Know which conclusions are visual observation, which came from records, and which a specialist tested. A broad repair allowance shouldn't replace a focused review of a failing major system.

## 2. Inspection Checklist
STEP 2 — WALK THE FACILITY, SYSTEM BY SYSTEM
Field Inspection Checklist
Start at the roof and follow the water. Sample repeated components across buildings, ages and orientations. Rate condition; flag what needs a specialist.
Component / item | Condition | Records reviewed? | Specialist needed? | Notes / location / quantity
ROOF & DRAINAGE
Roof material, age & repair history
Seams, fasteners, flashing, penetrations
Roof-to-wall transitions
Gutters, scuppers, drains, downspouts
Ponding, staining, active leaks
Discharge directed away from doors/slabs/neighbors
Warranty coverage & transferability
FOUNDATIONS, SLABS & PAVING
Foundation cracking, settlement, displacement
Slab heaving, spalling, uneven thresholds
Doors that bind or misalign (movement)
Wall-panel / masonry separation
Paving: surface aging vs. base failure
Trip hazards / accessibility barriers
Retaining walls, slopes, soil movement
SITE DRAINAGE
Prior flooding, ponding, water-intrusion history
Stormwater entering from neighboring property
Low unit thresholds / floor elevations
Catch basins, culverts, swales, detention
Access roads passable during storms
Shared-drainage maintenance obligations
BUILDING ENVELOPE
Wall panels, masonry, joints, sealants
Corrosion, loose fasteners, impact damage
Openings for water, pests or wind
Insulation condition (climate buildings)
Condensation, staining, odor
DOORS & HARDWARE
Operation, balance, alignment (sample widely)
Springs, drums, tracks, fasteners
Bottom seals / water entry
Corrosion, dents, wind damage
Latches, hasps, lock compatibility
Wind-rated components where required
Replacement-part availability
CLIMATE CONTROL
Equipment type, age, capacity, service history
Actual temp/humidity at distant & upper-floor units
Filters, coils, drains, condensate disposal
Controls, sensors, after-hours alarms
Envelope leakage / missing insulation
Condensation, corrosion, mold-like growth
ELECTRICAL & PLUMBING
Service capacity & main equipment
Panels, labeling, visible unsafe work
Interior/exterior, emergency lighting, exit signs
Office/restroom/utility plumbing; leaks; shutoffs
FIRE & LIFE SAFETY
Sprinklers, alarms, hydrants, extinguishers
Inspection/testing/maintenance records current
Emergency access & clear fire lanes
Egress paths, exit hardware, signage
Known violations / open permits
ELEVATORS & LIFTS
Inspection certificate & open violations
Service contract & maintenance logs
Shutdown / entrapment history
Parts availability & vendor support
Modernization / replacement outlook
GATES & ACCESS CONTROL
Gate operator age, cycle count, service history
Safety devices (photo eyes, loops, edges)
Keypads, controllers, credentials, PMS integration
Delinquency lockout & manual override
Backup power & emergency access
CAMERAS, LIGHTING & ALARMS
Camera coverage, blind spots, image quality
Recording retention & retrieval; night performance
Lighting outages / dark areas
Alarm zones, monitoring, incident history
Account/credential ownership & transfer
FENCING & PERIMETER
Fence condition, height, climb/impact points
Vegetation blocking cameras / concealment
Drainage openings / low areas
ACCESSIBILITY (ADA)
Accessible parking, routes, slopes, entrances
Office counters, restrooms, elevators, controls, units
Barriers, correction costs, triggers from planned work
PEST & MOISTURE
Rodent/insect/bird evidence & entry points
Pest-control logs / repeat service areas
Moisture staining, odor, condensation
HAZARD EXPOSURE (regional)
Applicable hazards: snow/wind/hail/wildfire/hurricane/quake/heat/freeze
Insurance availability, limits, deductibles, mitigation
TRUCK & TRAILER ACCESS
Entrance width, visibility, turning; gate stacking off-road
Internal radii, corners, bollards, clearances
Dead ends / turnarounds; fire lanes
Pavement capacity; winter access

## 3. Records Request
STEP 3 — READ THE RECORDS BEHIND THE VISIBLE CONDITION
Records Request
Fresh coating or sealant can be sound maintenance — or it can hide the age and extent of a recurring problem. Compare the paper trail with the site.
Record | Obtained? | Reference / notes
Roof, paving & door invoices
HVAC, gate & security service logs
Elevator & fire-system records
Preventive-maintenance schedules
Utility bills
Insurance claims & loss runs
Tenant complaints (leaks, access, security)
Permits, warranties & certificates
Capital budgets & postponed projects
Vendor recommendations declined by the seller
Storm/flood/damage photographs

## 4. Component Register
STEP 4 — RATE REMAINING USEFUL LIFE, PRICE THE WORK
Component Register & Remaining Useful Life
For each major component, record age, condition, RUL, quantity and unit cost. Extended cost computes and feeds the capital plan. Avoid false precision, use ranges.
Component | System | Installed / Last-replaced | Expected service range | Observed condition | Maintenance history | RUL (yrs) | Recommended work | Qty | Unit Cost | Extended Cost | Expected Year | Consequence of delay | Confid- ence
Gate operator replacement (2 gates) | Security | 2014 | 10–15 yr | Poor | Frequent failures | 1 | Replace operators + safety devices | 2 | 6500 | 13000 | Immediate | Delinquency lockout unreliable | High
Fire panel repair & recertification | Fire | 2016 | — | Poor | Overdue testing | 1 | Repair, test, certify | 1 | 4500 | 4500 | Immediate | Life-safety / permit risk | High
Overhead door bottom seals | Doors | 2015 | 8–12 yr | Fair | Ad-hoc | 3 | Replace bottom seals | 150 | 45 | 6750 | Year 1 | Water entry at thresholds | Medium
Camera system + NVR upgrade | Security | 2015 | 7–10 yr | Fair | None | 2 | Replace NVR + cameras | 1 | 18000 | 18000 | Year 1 | Blind spots; weak evidence | Medium
Metal roof recoat | Roof | 2013 | 20–25 yr | Fair | 1 recoat | 6 | Elastomeric recoat | 40000 | 1.75 | 70000 | Year 2 | Leaks into tenant units | Medium
HVAC condenser replacement | Climate | 2012 | 12–15 yr | Fair | Annual PM | 3 | Replace 3 condensing units | 3 | 9000 | 27000 | Year 2 | Humidity / temp excursions | Medium
Asphalt mill & overlay + base repair | Paving | 2010 | 15–20 yr | Poor | Patches | 8 | Mill, base repair, overlay, restripe | 1 | 85000 | 85000 | Year 3 | Trip hazards; truck access | Medium
Elevator modernization | Elevator | 2004 | 20–25 yr | Fair | Contract | 5 | Modernize controls/leveling | 1 | 60000 | 60000 | Year 4 | Upper-floor units unserviceable | Low
[9 empty] | TOTAL | 284250

## 5. Five-Year Capital Plan
STEP 5 — PUT THE WORK ON A CALENDAR
Five-Year Repair & Capital Plan
Cost and timing belong together: a project six months after closing hits differently than the same one in year five. Includes escalation, contingency and lost rentals.
Escalation / inflation % (per year) |  | 3%
Contingency % (concealed / uncertain) |  | 10%
Timing | Yr index | Base Cost | Escalation Factor | Escalated Cost | Contingency | Disruption / Lost Rentals | Total
Immediate | 0 | 17500 | 1 | 17500 | 1750 | 0 | 19250
Year 1 | 0 | 24750 | 1 | 24750 | 2475 | 0 | 27225
Year 2 | 1 | 97000 | 1.03 | 99910 | 9991 | 3000 | 112901
Year 3 | 2 | 85000 | 1.0609 | 90176.5 | 9017.65 | 6000 | 105194.15
Year 4 | 3 | 60000 | 1.0927 | 65563.62 | 6556.362 | 4000 | 76119.982
Year 5 | 4 | 0 | 1.1255 | 0 | 0 | 0 | 0
TOTAL |  | 284250 |  | 297900.12 | 29790.012 | 13000 | 340690.132
Immediate repairs (at / soon after closing) |  |  | 19250
Near-term: Immediate + Year 1 |  |  | 46475
Five-year capital total (Years 1–5) |  |  | 321440.132
Total incl. immediate |  |  | 340690.132
Suggested average annual reserve (Years 1–5) |  |  | 64288.0264
CAPITAL BY SYSTEM (all years)
System | Total (all years)
Roof | 70000
Paving | 85000
Doors | 6750
Climate | 27000
Electrical | 0
Fire | 4500
Elevator | 60000
Security | 31000
Site/Drainage | 0
Envelope | 0
Other | 0

## 6. Warning Signs
A DEFECT NEEDS CONTEXT
Warning Signs
Many physical problems can be repaired or priced. The buyer needs a credible scope, timing, operating impact and funding plan before the issue becomes theirs.
Warning sign | Applies? | Resolved? | Scope / cost / notes
PCA is a short walkthrough with broad exclusions
Only one building / a few doors sampled without explanation
Roof age and repair history are unknown
Roof budget assumes coating will solve active water entry
Paving estimates exclude base repair or drainage correction
Outside a mapped flood zone but has water claims or ponding
Climate buildings show uneven conditions, odor or condensation
Fire or elevator records are missing or expired
Gate & camera systems depend on seller-controlled accounts
Recent repairs have no invoices, permits or warranties
Five-year schedule omits operational disruption / lost rentals
Model uses a small reserve with no itemized capital plan
Warning signs that apply | 0
…of those, still unresolved | 0
Final question: if every known repair and five-year capital item becomes yours at closing, do the price, reserves and operating plan still make sense?